## Slide 1
Load Flexibility
Preliminary Ice Storage Results for Metric Discussion
Ryan Meyer and Karl Heine
July ##, 2019

## Slide 2: Content Overview
Model Descriptions
Annual Metrics Comparison
Monthly Peak Demand Comparison
Average Daily Demand Profile Comparison
Load Duration Curve Comparison

## Slide 3: Model Descriptions
DOE Prototype Secondary School
  90.1-2010
  Climate Zone 2A
  Houston, TX
Cooling Plant
  Baseline
    Air-cooled chiller at 90.1-2010 minimum performance
  Ice Storage Models
    Air-cooled chiller at 70% of Baseline model capacity
    Discharge Window – 8 am to 8 pm Weekdays only
    Charging Window – 11 pm to 6 am
  Two Configurations
    Chiller placed upstream of ice storage tank
    Ice storage tank placed upstream of chiller

## Slide 4: Annual Metrics Comparison
Model | EUI |  | Facility Annual MWh |  | Cooling Annual MWh | 
Baseline | 68.3 | - | 3,091 | - | 1,192 | -
Chiller Upstream | 66.0 | -3% | 2,949 | -5% | 1,064 | -11%
Ice Tank Upstream | 66.7 | -2% | 2,992 | -3% | 1,108 | -7%

## Slide 5: Annual Metrics Comparison
Model | Facility Peak kW |  | Cooling Peak kW |  | Average Chiller COP | Runtime Hours
Baseline | 991.5 | - | 576.7 | - | 2.55 | 5947
Chiller Upstream | 834.4 | -16% | 419.7 | -27% | 3.07 | 5764
Ice Tank Upstream | 793.4 | -20% | 371.8 | -36% | 2.94 | 6237

## Slide 6: Monthly Peak Demand Comparison
Baseline (No Ice) Chiller Upstream Ice Upstream
kW

## Slide 7: Average Daily Demand Profile Comparison
Baseline (No Ice) Chiller Upstream Ice Upstream
kW

## Slide 8: Load Duration Curve Comparison
Baseline (No Ice) Chiller Upstream Ice Upstream
kW

## Slide 9: Load Duration Curve Comparison
Baseline (No Ice) Chiller Upstream Ice Upstream
kW