## Slide 1
Modeling Thermal Energy Storage
Karl Heine
Colorado School of Mines

## Slide 2: Agenda
Motivation: Modeling Challenges
Improving the Models
Identifying Potential Benefits
Example Results
Distributed Ice Storage Systems

## Slide 3: Modeling Challenges
Models are Tedious to Build
  TES is ignored as a design option
Implementing Control Strategies Not Obvious
  “Optimal” operating points unidentifiable
  Imposing power limits on hardware not easy
Limited Performance Data Available
  Generic curves used

## Slide 4: Improving Models
Goal: Make ASHRAE Design Guide for Cool Thermal Storage recommendations available to energy modelers using EnergyPlus
  Design Configuration Options
  Storage Objective Options
  High-level Operating Strategy Options
  Provide Load Limiting Options on Chiller
Method: OpenStudio Measure Scripting

## Slide 5: Potential Benefits of Ice Thermal Storage
Chiller Downsizing
  Reduced Capital Costs
  Higher Average Part-Load Operation
Improved Average Efficiency
Reduction in Annual Electricity Use!
Effective Load-Shifting Out of On-Peak Hours
Controllable Energy Storage

## Slide 6: Example Results Central Ice
School with Air-Cooled Chiller in Houston (TMY3)
DOE Prototype 90.1-2010 Model with Modifications:
  Hardware:
    Chiller Downsized by 30%
    2000 Ton-Hours of Ice
  Configuration: Chiller Upstream of Ice Tank
  High Level Control Strategy:
    Ice Priority up to 30% of Design Load
    0800-2000 on Weekdays
  Chiller Limit: 65% of Nominal Capacity During Ice Discharge

## Slide 7: Average Daily Profile for Facility Electric Load
Baseline With Ice Storage
kWe

## Slide 8: Maximum Monthly Facility Electric Demand
Baseline With Ice Storage
kWe

## Slide 9: Results Summary
Model | EUI [kWh/m2] | Chiller Annual Electricity [MWh] | Chiller Average COP | Chiller Runtime Hours
School Baseline | 157.7 | 973 | 2.55 | 5947
School With Ice* | 150.5 (-4%) | 845 (-23%) | 3.07 (+20%) | 5768 (-3%)
* Includes downsized chiller yet produced no change in unmet-hours from baseline model.

## Slide 10: Distributed Ice Storage
Unitary Thermal Storage Systems (UTSS) provide smaller-scale, distributed ice storage solutions
40 ton-hour ice batteries
Up to 15 tons cooling from ice unit
Compatible with 3-20 ton commercial AC units
4-6 hours of shifted cooling load
Adds cooling coil to air stream

## Slide 11: Example Results Distributed Ice
Stand-Alone Retail with 4 RTU’s
DOE Prototype Models in 15 Climate Zones (TMY3)
Ice Batteries Added to Each RTU
Sized to Meet Climate Zone-Specific Loads
Utility Rates with 5-6 Hour Daily On-Peak Price Periods

## Slide 12: Economic Impact of Distributed Ice Storage
Chart: Time-of-Day
| 0 | 0.33332175925925928 | 0.33333333333333331 | 0.49998842592592596 | 0.5 | 0.74998842592592585 | 0.75 | 0.87498842592592585 | 0.875 | 0.99998842592592585
PG&E E19 | 0 | 0 | 3.11 | 3.11 | 12.42 | 12.42 | 3.11 | 3.11 | 0 | 0
SRP E32 | 1 | 1 | 1 | 1 | 6.65 | 6.65 | 1 | 1 | 1 | 1
Chart: Time of Day
| 0 | 0.33332175925925928 | 0.33333333333333331 | 0.49998842592592596 | 0.5 | 0.74998842592592585 | 0.75 | 0.87498842592592585 | 0.875 | 0.99998842592592585
PG&E E19 | 0.07631 | 0.07631 | 0.09298 | 0.09298 | 0.10559 | 0.10559 | 0.09298 | 0.09298 | 0.07631 | 0.07631
SRP E32 | 0.0558 | 0.0558 | 0.1113 | 0.1113 | 0.1691 | 0.1691 | 0.1113 | 0.1113 | 0.0558 | 0.0558

## Slide 13: Electricity Bill Savings with Distributed Ice
Chart: Climate Zone
| 1A | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8B
Retail - PG&E | 0.078923 | 0.10237 | 0.09032 | 0.1015 | 0.086023 | 0.061282 | 0.095176 | 0.076954 | 0.088085 | 0.083744 | 0.086316 | 0.072623 | 0.068601 | 0.067443 | 0.035106
Retail - SRP | 0.089806 | 0.11534 | 0.12112 | 0.10998 | 0.094901 | 0.043585 | 0.09754 | 0.079387 | 0.07831 | 0.083353 | 0.080203 | 0.067699 | 0.059227 | 0.054781 | 0.026756

## Slide 14: Summary
Modeling Challenges
Improving the Models
Identifying Potential Benefits
Example Results
Distributed Ice Storage Systems

## Slide 15
Questions?
Karl Heine
kheine@mines.edu