## Slide 1
Load Flexibility Measure:
Central Ice Storage
Preliminary Measure Discussion
September 20, 2019

## Slide 2: Objectives of the Measure
Implement rapid and accurate modeling solution for evaluation of ice storage using building energy models
Permits parametric analysis of design and control options
Implements ASHRAE Design Guide for Cool Thermal Storage configuration options and recommended controls

## Slide 3: User Inputs
Partial Storage
Full Storage
Chiller Upstream
Storage Upstream
Inside Melt
Outside Melt

## Slide 4: User Inputs
Chiller Downsizing
Chiller De-Rate
During Ice Discharge

## Slide 5: User Inputs
Setpoint Between Chiller and Ice Tank

## Slide 6: Multiple Ways to Achieve Controls
Documentation provides “recipes” translating Design Guide terms into measure inputs
  Full Storage
  Partial Storage
    Load Leveling
    Demand Limiting
    Ice Priority
    Chiller Priority

## Slide 7: Discussion

## Slide 8
Thank you!

## Slide 9: Model 2: Partial Storage Secondary School
Secondary School (2010):
Climate zone 2A
Houston, TX weather (TMY3)
210,000 ft2 conditioned space
Air-cooled screw chiller (downsized)
2000 ton-hours of ice storage
Chiller-upstream, storage-priority 0800-2000 on weekdays

## Slide 10: Secondary School: Chiller Electric Power
Baseline CTES
kWe

## Slide 11: Secondary School: Facility Electric Power
kWe
Baseline CTES

## Slide 12: Secondary School: Monthly Peak Demand
kWe
Baseline CTES

## Slide 13: Secondary School: Ice Use
State of Charge

## Slide 14: Secondary School: Facility Load Duration
Baseline CTES
kWe

## Slide 15: Results Summary
Model | EUI [kWh/m2] | Facility Annual Electricity [MWh] | Chiller Annual Electricity [MWh]
School Baseline | 157.7 | 3,091 | 973
School Partial Storage | 150.5 (-4%) | 2,948 (-4%) | 845 (-23%)

## Slide 16: Results Summary
Model | Min Ice SoC | Chiller Size [tons] | Average Chiller COP | Runtime Hours
School Baseline | - | 578 | 2.55 | 5947
School Partial Storage | 11% | 405 (-30%) | 3.07 (+20%) | 5768 (-3%)

## Slide 17: Full Storage
Select: Full Storage
Select: Partial Storage, Storage Upstream
  Storage (Ice) Setpoint = Loop Setpoint
Select: Partial Storage, Chiller Upstream
  Chiller Setpoint = Loop Setpoint + Loop Design T
  Chiller Limiter = 0.0

## Slide 18: Partial Storage: Load Leveling
Select: Chiller Upstream, Downsize Chiller
  Chiller Setpoint = Loop Setpoint
  Requires Iteration to “Level” the Load

## Slide 19: Partial Storage: Demand Limiting
Select: Chiller Upstream, Apply Chiller Limiter
  Uses Fraction to Set Max T Across Chiller
  Will Not Exceed Limit, Even if Ice Runs Out
Select: Storage Upstream, Set T Across Chiller
  Chiller Will Meet Load if Ice Runs Out

## Slide 20: Discharge Priorities
Configuration Matters:
Chiller Priority –> Select Storage Upstream
  Chiller Meets Load First, Up to a Maximum Value
  Chiller Load More Uniform
Storage Priority –> Select Chiller Upstream
  Ice Meets Load First, Up to a Maximum Value
  Ice Usage More Uniform

## Slide 21: Baseloading with Multiple Chillers
Select: Single Chiller on Multiple-Chiller Loop
  Modifies Loop Setpoint Manager
  Modifies Selected Branch Components
  Limited Testing to Date

## Slide 22: EMS Script: Chiller Limiter
ICE_AV: Ice Availability (On/Off)
SP: Chiller Setpoint Temperature
SWT_SP: Supply Water Setpoint Temperature
EEWT: Evaporator Entering Water Temperature
dt_max: Max Temperature Difference on Chiller
ELWT: Evaporator Leaving Water Temperature Setpoint Actuator
Limit_Counter: Instances of Limiter Use